## Fire Pump Test Data
2005 Dr. Martin Luther King Jr. Dr.
Indianapolis, IN 46202
(317) 925-9661
www.PeerlessPump.com
Project Name: |  |  | Home Depot 0526 Corpus Christi TX | [11 empty] | Address: | 5041 S Padre Island Dr
Project Description |  |  | Electric Splt Case | [7 empty] | Serial No. | 9927226906 |  |  |  | Corpus Christi, Texas 78411
City - State - Zip |  |  | Corpus Christi, Texas 78411 | [7 empty] | Start-up Date: | 2026-02-26
Fire Pump Flow Test Data
1. | Pump / Driver / Controller | [13 empty] | Driver Rep. |  | Michael Phears
General Contractor | [6 empty] | Peerless Rep. |  |  | Michael Phears |  |  |  |  | Controller Rep. |  | Michael Phears
|  |  |  | ph. | [6 empty] | ph. | 281-772-6451
Insurance / Fire Department Rep. |  |  |  |  | Corpus Fire Dept |  | Jockey Pump Start PSI |  |  |  |  | 160 |  |  | Auto Start |  |  | 6
Brian Rogers |  |  |  | ph. | 361-739-3545 |  | Jockey Pump Stop PSI |  |  |  |  | 170 |  |  | Manual Start |  |  | 6
Sprinkler Contractor |  |  |  | Western States |  |  | Fire Pump Start PSI |  |  |  |  | 150 |  |  | Timer Setting |  |  | n/a
Adam |  |  |  | ph. |  |  | Fire Pump Stop PSI |  |  |  |  | 160 |  |  | Transfer Switch |  |  | n/a
Engineering Firm Rep. | [6 empty] | Automatic Operator Work |  |  |  |  | yes |  |  | Suction Size |  |  | 8
|  |  |  | ph. |  |  | Manual Operator Work |  |  |  |  | yes |  |  | Discharge Size |  |  | 6
|  | PUMP | [5 empty] | DRIVER | [5 empty] | CONTROLLER
Pump Type |  |  |  | Split Case |  | Driver Type |  |  | Electric |  |  | Controller Type |  |  |  | Electric
Pump Manufacturer |  |  |  | Peerless |  | Driver Manufacturer |  |  | Weg |  |  | Controller Manufacturer |  |  |  | Firetrol
Pump Serial Number |  |  |  | 50028220 |  | Driver Serial Number |  |  | 11166711194 |  |  | Controller Serial Number |  |  |  | FZ1258856
Pump Model Number |  |  |  | 6AEF10 |  | Driver Model Number |  |  | 125360P3EFP404TS-W40 |  |  | Controller Model Number |  |  |  | FTA1930-AM125B
Pump Rated GPM |  |  |  | 1500 |  | Driver Horse Power |  |  | 125 |  |  | Controller Horse Power |  |  |  | 125
Pump Rated PSI |  |  |  | 110 |  | Driver RPM |  |  | 3545 |  |  | Controller Volts |  |  |  | 460
Pump Rated RPM |  |  |  | 3550 |  | Driver Volts |  |  | 230/460 |  |  | Controller Phase |  |  |  | 3
Pump Maximum PSI |  |  |  | 138 |  | Driver Amps |  |  | 274/137 |  |  | Controller Cycles |  |  |  | 60
Pump Pressure at 150% |  |  |  | 80 |  | Driver Phase |  |  | 3 |  |  | Controller Interrupt Cap
Pump Impeller Size |  |  |  | 8.29 |  | Driver Cycles |  |  | 60 |  |  | Controller Diesel Volts |  |  |  | n/a
Pump Stages |  |  |  | 1 |  | Driver Service Factor |  |  | 1.15 |  |  | Controller Diesel Ground |  |  |  | n/a
FIRE PUMP TEST DATA
Speed |  | Suction |  | Discharge |  | Net |  |  |  | Streams |  |  |  |  | Total |  | % | Volts | Amps
Rpm |  | Pressure |  | Pressure |  | Head | Size |  | Pitot Readings | [5 empty] | GPM |  | Rated
|  | Psi |  | Psi |  | Psi |  | #1 | #2 | #3 | #4 | #5 | #6 | #7 |  |  | Capacity
3574 |  | 52 |  | 192 |  | 140 | 2.5 | CHURN | [6 empty] | 0 |  | 0%
3560 |  | 34 |  | 144 |  | 110 | 2.5 | 5 | 5 | 5 |  |  |  |  | 1522.0542 |  | 101.5%
3555 |  | 15 |  | 96 |  | 81 | 2.5 | 11 | 11 | 11 |  |  |  |  | 2257.5711 |  | 150.5%
[7 empty] | 2.5 | [7 empty] | 0 |  | 0%
[7 empty] | 2.5 | [7 empty] | 0 |  | 0%
Readings Marked (+) in Shaded Column are Heads Above Atmosphere. Those Marked (-) are Lifts. For Vertical Shaft Pumps omit Suction Pressure and Net Head Readings.
Approval Signatures
|  |  |  | Name | [5 empty] | Signature | [6 empty] | Date
Peerless Pump Rep. |  |  |  | Michael Phears | [12 empty] | 2026-02-26
|  |  |  | Name | [5 empty] | Signature | [6 empty] | Date
Sprinkler Contractor
|  |  |  | Name | [5 empty] | Signature | [6 empty] | Date
General Contractor
|  |  |  | Name | [5 empty] | Signature | [6 empty] | Date
Insurance / Fire Dept. Rep.
|  |  |  | Name | [5 empty] | Signature | [6 empty] | Date
Engineering Firm Rep.

## Acceptance Test Curve
Project: | Home Depot 0526 Corpus Christi TX |  |  |  | FIRE PUMP TEST RESULTS ON NET BASIS | [17 empty] | gpm | psi
Location: | Corpus Christi, Texas 78411 |  |  |  | Pump ID: |  | Split Case |  |  |  | Rated Flow: | 1500 | Rated Pressure: |  | 110 | Rated Speed: |  | 3550 | Suction Size(in.): |  | 8 | Churn Rating | 0 | 132
[5 empty] | Make: |  | Peerless |  |  |  | Model: | 6AEF10 |  |  | Serial No.: | 50028220 |  |  | Discharge Size(in.): |  | 6 | 100% Rating | 1500 | 110
[22 empty] | 150% Rating | 2250 | 71.5
Pump | Flowing | [8 empty] | Flow- | Combined | Pressure |  | Vel. | Net | Pump | Corr. to Rated Speed
Test | Outlet I.D.* | Cd* | [7 empty] | meter | Flow | Suction | Discharge | Head | Pressure | Speed | Flow | Pressure | Volts | Amps
Date | (i.e.1 1/8"=1.125") |  | Pitot Readings* - (psi) | [6 empty] | (gpm) | (gpm) | (psi) | (psi) | Corr. | (psi) | (rpm) | (gpm) | (psi) | (v) | (A)
| 2.5 | 1.217 | CHURN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 192 | 0 | 140 | 3574 | 0 | 138.1261 | 0 | 0
| 2.5 | 1.217 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 1522.0542 | 34 | 144 | 1.3722 | 111.3722 | 3560 | 1517.7787 | 110.7474 | 0 | 0
| 2.5 | 1.217 | 11 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 2257.5711 | 15 | 96 | 3.0189 | 84.0189 | 3555 | 2254.3959 | 83.7828 | 0 | 0
| 2.5 | 1.217 | [7 empty] | (psi): 0; (rpm): 0; (v): 0; (A): 0
| 2.5 | 1.217 | [7 empty] | (psi): #VALUE!; (rpm): 0; (v): 0; (A): 0
| 0 | 1.217 | [7 empty] | (psi): #VALUE!; (rpm): 0; (v): 0; (A): 0
*NOTE: Flowing Outlet I.D. must be 1.125", 1.75" or 2.5". The conversion of pitot readings to a flowrate is automatic based on Cd of Underwriter's Playpipes for 1.125" & 1.75" or a Cd of smooth, rounded 2.5" outlet.
Note on H2: Pump ID: Insert name or number of pump for identification purposes.
Note on M2: Rated Flow: 100% Design Flow Rating.
Note on P2: Rated Pressure: Pressure Rating at 100% Design Flow.
Note on S2: Rated Speed: Pump Speed Rating at 100% Design Flow and 100% Design Pressure.
Note on V2: Suction Size: Diameter of pump suction inlet flange.
Note on V3: Discharge Size: Diameter of pump discharge outlet flange.
Note on H4: Suction Source: Indicate where pump suction is from and related size. (i.e. 250,000 gal. suction tank, 12" PWM in Gilman St., etc.)
Note on A8: Test Date: Date of test . (i.e. 9/12/98 Test)
Note on A9: Name: Name of Loss Prevention Consultant.
Note on B9: Flowing Outlet: The automatic conversion of pitot readings will only work with 1.125", 1.75" or 2.5" outlets. Any other sizes will need to be manually converted and entered under the Flowmeter column.
Note on T9: Volts: Actual voltage rating for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test. (i.e. 435, 440,437)
Note on U9: Amps: Actual amperage reading for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test.
Note on B10: Flowing Outlet: The automatic conversion of pitot readings will only work with 1.125", 1.75" or 2.5" outlets. Any other sizes will need to be manually converted and entered under the Flowmeter column.
Note on T10: Volts: Actual voltage rating for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test. (i.e. 435, 440,437)
Note on U10: Amps: Actual amperage reading for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test.
Note on B11: Flowing Outlet: The automatic conversion of pitot readings will only work with 1.125", 1.75" or 2.5" outlets. Any other sizes will need to be manually converted and entered under the Flowmeter column.
Note on T11: Volts: Actual voltage rating for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test. (i.e. 435, 440,437)
Note on U11: Amps: Actual amperage reading for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test.
Note on B12: Flowing Outlet: The automatic conversion of pitot readings will only work with 1.125", 1.75" or 2.5" outlets. Any other sizes will need to be manually converted and entered under the Flowmeter column.
Note on T12: Volts: Actual voltage rating for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test. (i.e. 435, 440,437)
Note on U12: Amps: Actual amperage reading for each motor phase on electric motor driven pumps. Usually only recorded at initial acceptance test.
Note on A15: Test Date: Date of test . (i.e. 9/12/98 Test)

## Field Data Sheet
Speed | Suction | Discharge | Dia | Pitot Pressure |  |  | Flow | Volts |  | Amps
|  |  | 2.50 | CHURN |  |  | 0
2.50
2.50
|  |  |  | Engine | Full Load |  |  |  | % | GPM | Pito PSI | TDH
Jockey Pump Start: |  |  |  | RPM |  |  |  |  | Churn | 0 | 0 | 138
Jockey Pump Stop: |  |  |  | Oil Press |  | Starts |  |  | 100 | 1509 | 3@5 | 110
|  |  |  | Temp |  | Manual | Auto |  | 150 | 2259 | 3@11 | 80 | 0r 2248 | 4@6.14
Fire Pump Stop: |  |  |  | Damper T
Final Hour
|  |  |  | Bearing | Temp
NOTES: |  |  |  | Start | Stop
Indoard
Outboard

## Revison Log
Revision Number | Changes
1 | Changed formual references to named values.
Added additional data fields.
2.0 | Removed all that stuff.